## Project Data Sheet
FUJITSU AISTAGE VR-II 208/230V PRE-COMMISSIONING REPORT (HEAT RECOVERY ONLY)
Please note: Fujitsu Commissioning Agent will not visit/commission a job until the pre-commissioning forms are completely filled out, and the system has been started and confirmed to be operating normally.
Project Name:
Airstage Project Manager Project ID #:
| Installing Contractor: |  |  |  | Phone:
Contractor Address:
|  | City: | State: |  | Postal Code:
| Fujitsu Distributor: |  |  | Phone:
| Fujitsu Airstage Rep: |  |  | Phone:
| Report Completed By: |  |  | Phone:
|  | Date: |  | Email:
Project and System Data
Total Number of Refrigerant Circuits:
Total Number of Condensing Units:
Total Number of RBUs:
Total Number of Indoor Units:
Comments

## Control Wiring Setup
** This page must be completed only once for the entire project
Complete Prior to Powering System On
Project Name: | 0
Control Wiring Setup
Check Item | Check Contents | Target Value | Actual Value
VRF Network Transmission System | Transmission Wire | Is it LonWorks compatible?
Wire Manufacturer and Model
| Transmission Wire Type | 22 AWG (0.33 mm2) Level 4 (NEMA) Non-polar 2 Core, Shielded, Twisted Pair Solid Core Diameter 0.026 in. (0.65mm)
| Connection Terminals | Between IU and RBU
(Terminal: X1 & X2)
Between RBU and Master OU
(Terminal: X1 & X2)
Between Master and Slave / Slave and Slave
(Terminal: H1 & H2)
Between Master Outdoor Units
(Terminal: Z1 & Z2)
Are both ends of shield wire grounded?
Wiring connections per terminal? (Must be ≤ 2)
| Total Transmission Wire Length | ≤ 11811 ft
| Network Wiring Layout | No Loops
| No. of Network Segment(s) | -
Yes
No
Yes
No
Loop
Does Not Loop

## Control Wire Resistance Check
** This page must be completed only once for the entire project
Complete Prior to Powering System On
Project Name: | 0
Control Wire Resistance Check
Check resistance at both ends of the communication line, from the device with the terminal resistor (Outdoor Unit or Signal Amplifier) to the most distance device
Unit | Outdoor Unit | SA #1 | SA #2 | SA #3 | SA #4 | SA #5 | SA #6 | SA #7 | SA #8
Resistance (Ohms)

## Controls Configuration
** This page must be completed only once for the entire project
Complete Prior to Powering System On
Project Name: | 0
Controls Configuration
Check Item | Check Contents | Target Value | Actual Value
VRF Network Controls System | Addressing Method | Manual/Automatic
| No. of Outdoor Units | ≤ 100
No. of RBUs
| No. of Indoor Units | ≤ 400
| No. of System Controllers (or SC Lite) | Max. One per VRF Network System
| No. of Touch Panel Controllers | Total 16 Max. per VRF Network System
No. of Central Remote Controllers
| No. of Signal Amplifiers (≤ 8) | One per 1640 ft transmission line length / One per 1312 ft transmission line length between units / One per every 64 number of units / One per Network Segment
| No. of Network Convertors | 100 Max. per VRF Network System
| No. of BACnet Gateway | Max. One per VRF Network Systems
| No. of Convertors for LonWorks | Max. One per System (IU ≤ 128, OU ≤ 100)
| Terminal Resistors | One per Network Segment

## Electrical Supply
** This page must be completed for each system / refrigerant circuit on the project
Complete Prior to Powering System On
Project Name: | 0 |  | System Designation:
Electrical Supply
Check Item |  | Check Contents | Target Value | Unit | Actual Value
Incoming Power | Outdoor Unit(s) | Circuit Breaker Capacity | 6 or 8 Ton OU: 50 A 10 Ton OU: 60A | Master:
Slave-1:
Slave-2:
If 50 A or 60 A breaker is unavailable, are you using a larger breaker along with a fused disconnect with 50 A or 60 A fuses?
|  | GFEB | Are GFEBs installed for all circuits? | All Units
(Ground Fault Equipment Breaker)
|  | Power Line Wire Size: AWG | As per local code | Master:
Slave-1:
Slave-2:
|  | Actual Power Supply (V) | 187-253 V between each leg | Master:
|  | (Between R-S/S-T/T-R) |  | Slave-1:
|  | (208-230/3/60) |  | Slave-2:
| Indoor Units | Number of Indoor Circuits
|  | GFEB | Are GFEBs installed for all circuits? | All Units
(Ground Fault Equipment Breaker)
|  | Circuit Breaker Capacity | 15 A | Circuit #1
|  | Power Line Wire Size | 12 AWG
|  | Supply Voltage | 187-253 V
|  | Circuit Breaker Capacity | 15 A | Circuit #2
|  | Power Line Wire Size | 12 AWG
|  | Supply Voltage | 187-253 V
|  | Circuit Breaker Capacity | 15 A | Circuit #3
|  | Power Line Wire Size | 12 AWG
|  | Supply Voltage | 187-253 V
|  | Circuit Breaker Capacity | 15 A | Circuit #4
|  | Power Line Wire Size | 12 AWG
|  | Supply Voltage | 187-253 V
|  | Circuit Breaker Capacity | 15 A | Circuit #5
|  | Power Line Wire Size | 12 AWG
|  | Supply Voltage | 187-253 V
|  | Circuit Breaker Capacity | 15 A | Circuit #6
|  | Power Line Wire Size | 12 AWG
|  | Supply Voltage | 187-253 V
Yes
No
N/A
Yes
No
Yes
No

## Outdoor Unit Setup
** This page must be completed for each system / refrigerant circuit on the project
Complete Prior to Powering System On
Project Name: | 0 |  | System Designation: | 0
Outdoor Unit Setup
Check Item |  | Check Contents | Target Value | Unit | Actual Value
Outdoor Unit(s) | Gereral Installation Data | Model Name |  | Master
Slave 1
Slave 2
|  | Serial Number |  | Master
Slave 1
Slave 2
|  | Master Outdoor Unit Configuration | Largest capacity Outdoor Unit set as Master?
Master Outdoor Unit is closest to indoor units?
|  | Elevation | All Outdoor Units elevated above average snow level?
|  | Refrigerant Piping | Insulated properly without gap?
| Address Settings | DIP Switch Setting |  |  | Check All That Apply
|  |  | Outdoor Unit Address SET 3-1 & SET 3-2 (Setting for Master & Slave Units) (Default: OFF-OFF) | Master (OFF-OFF)
Slave-1 (OFF-ON)
Slave-2 (ON-OFF)
|  |  | Number of Slave Units SET 3-3 & SET 3-4 (Set On Master Only) (Default: OFF-OFF) | No Slave (OFF-OFF)
1 Slave (OFF-ON)
2 Slaves (ON-OFF)
|  |  | Number of Outdoor Units SET 5-1 & SET 5-2 (Setting for Master & Slave Units) (Default: OFF-OFF) | 1 OU (OFF-OFF)
2 OU (OFF-ON)
3 OU (ON-OFF)
|  |  | Terminal Resistor SET 5-4 (Setting for Master Unit Only) (Default: OFF) | OFF or ON
|  | Rotary Dial Setting | Refrigerant Address (Setting for Master & Slave Units) | REF AD x10 & REF AD x1
| Refrigerant Piping | Gas & Liquid Pipe Service Valves Open Completely? |  | Master
Slave 1
Slave 2
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
OFF
ON

## RBU Setup
** This page must be completed for each system / refrigerant circuit on the project
Complete Prior to Powering System On
Project Name: |  | 0 |  | System Designation: |  | 0
RBU Setup
RBU |  |  | DIP-SW setting (OFF/ON) |  |  |  | Rotary-SW setting
|  |  | Operation Mode Selection |  | Cool/Heat Switch Control Time |  | Ref Address | RBU Address
Description | Model | Serial Number | SET 2-1 (Default: OFF) | SET 2-2 (Default: OFF) | SET 2-3 (Default: OFF) | SET 2-4 (Default: OFF) | REF AD x10 x1 | RBU AD x10 x1
OFF
ON
OFF
ON
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
ON
OFF
ON
OFF
ON
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF

## Indoor Unit Setup
** This page must be completed for each system / refrigerant circuit on the project
Complete Prior to Powering System On
Project Name: |  | 0 |  |  |  |  | System Designation: |  | 0
Indoor Unit Setup
Indoor Unit |  |  | Remote Type | DIP-SW setting (OFF/ON) | [6 empty] | Rotary-SW setting
|  |  |  | 2 Wire or 3 Wire Remote | External Input (Edge/Pulse) | Heater Fan Setting | Wireless RC Custom Code SW1 | Wireless RC Custom Code SW2 | Drain Pump SW (for Slim Duct) | Autolouver SW (for Slim Duct) | Ref Address | Indoor Unit Address | Remote Control Address
Description | Model | Serial Number | Simple, 3-wire, Individual Touch, Wireless, None | SW1 (Default: 2 Wire) | SET2-2 (Default: OFF) | SET 2-3 (Default: OFF) | SET 3-1 (Default: OFF) | SET 3-2 (Default: OFF) | SET 4-1 (Default: OFF) | SET 4-2 (Default: OFF) | REF AD x10 x1 | IU AD x10 x1 | RC AD
OFF
ON
OFF
ON
OFF
ON
OFF
ON
OFF
ON
OFF
ON
OFF
ON
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
OFF
OFF
ON
OFF
2 Wire
3 Wire
2 Wire
3 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire
2 Wire
2 Wire
3 Wire
2 Wire

## Ref Piping Config
** This page must be completed for each system / refrigerant circuit on the project
Complete Prior to Powering System On
Project Name: | 0 | System Designation: | 0
Refrigerant Piping Configuration
Check Item | Check Contents | Target Value | Actual Value
VRF Refrigerant Piping Configuration | Pipe Insulation | Are the lines properly insulated?
| Pipe Support | Are the lines properly supported?
| Suction Line Filter | Is there any filter in the suction line?
| Oil Trap | Are there any oil traps in the suction line?
| Moisture Prevention | Refrigerant pipes purged with nitrogen?
| Leak Test | System pressurized with nitrogen to 600 PSI and all fittings checked for leaks with soap bubble test?
| Evacuation | Industry standard “best practices” evacuation performed (vacuum of 500 microns held for 60 minutes)?
| Actual Pipe Length | Between Master OU and farthest IU (≤ 541 ft)
Between first separation tube and farthest IU (≤ 196 ft)
Total Pipe Length (≤ 2296 ft for one OU system; ≤ 3280 ft for multiple OU system)
Between OU and OU branch kit (≤ 9 ft)
Between Slave OU(s) and Master OU branch kit (≤ 39 ft)
| Height Difference | Between OU and IU (≤ 164 ft if IU is below OU; ≤ 131 ft if IU is above OU)
Between IUs (≤ 49 ft)
Between RBU and IU (≤ 16 ft)
Between RBUs (≤ 49 ft)
Between OUs (≤ 1 ft)
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No

## Ref Charge Calc
** This page must be completed for each system / refrigerant circuit on the project
208/230V HEAT RECOVERY ONLY
Complete Prior to Powering System On
Project Name: | 0 |  | System Designation: | 0
Additional Refrigerant Calculation
Check Item | Check Contents |  | Target Value | Actual Value
Additional Refrigerant Charge | Liquid Pipe Length (Actual Amount of Pipe Used on System, Not from Design Simulator) |  | Additional Refrigerant Amount for Liquid Pipe | A X B
|  | A | B
| Φ 1/4 in |  | 0.014 | 0
| Φ 3/8 in |  | 0.039 | 0
| Φ 1/2 in |  | 0.077 | 0
| Φ 5/8 in |  | 0.12 | 0
| Φ 3/4 in |  | 0.18 | 0
| # of 6 or 8 Ton Outdoor units (A) |  | Additional amout per OU (B) | 0
6.61
| # of 10 Ton Outdoor units (A) |  | Additional amout per OU (B) | 0
14.99
Total Additional Refrigerant to be Added to System |  |  |  | 0
Factory Charge Calculation
Total Factory Charge | Number of Outdoor Units on Refrigeration Circuit (1-3) |  | Factory Charge per Unit | Total Factory Charge
| A |  | B | A X B
|  |  | 26.01 | 0
Total System Charge Calculation and Check
Total System Charge and Check | Total System Charge |  |  | 0
Total Additional Refrigerant To Be Added + Total Factory Charge
| Does the Total System Charge Exceed the Design Limits? (Y / N) |  | For 1 outdoor unit system : ≤ 77.16 lb
For 2 outdoor unit system : ≤ 154.32 lb
For 3 outdoor unit system : ≤ 231.49 lb
****Write Total System Charge (Factory + Additional) on the Inside of the Front Panel of the Master Outdoor Unit****
Yes
No

## OU & IU Function Setting
** This page must be completed for each system / refrigerant circuit on the project
Complete After Powering System On
Project Name: | 0 | System Designation: |  | 0
Function Settings
Check Contents | Target Value |  |  |  | Actual Value
Outdoor Unit Circuit Breaker ON | Check Lighting of PCB: |  |  |  | LED101:
| LED101 (Green Light ON) & 7-SEG (no light) |  |  |  | 7-SEG:
Indoor Unit and RBU Circuit Breaker ON | All RBU LEDs are green
Check whether or not IU operation & timer lamps flash alternately
Outdoor Unit Function Setting (To Be Set on Master Outdoor Unit) | Are the necessary functions set? | Function Name |  |  | Function Value (e.g. F2:21:02)
Pipe Length
|  | Cooling Capacity Shift |  | Y / N
|  | Heating Capacity Shift |  | Y / N
|  | Operation Mode Setting Method |  | Y / N
|  | Snow Falling Protection Fan Mode |  | Y / N
|  | High Static Pressure Mode |  | Y / N
|  | Energy Saving Level Setting |  | Y / N
|  | Capacity Priority Setting |  | Y / N
|  | Low Noise Setting |  | Y / N
|  | Temperature Unit & Pressure Unit Setting |  | Y / N
|  | Others |  | Y / N
Indoor Unit function setting | Are the necessary functions set? | IU Model Name | Address | Function Name | Function Value
Yes
No
Yes
No